## 03-31-10
LOWER FOUNTAIN METROPOLITAN SEWAGE DISPOSAL DISTRICT
HAROLD D. THOMPSON REGIONAL WATER RECLAMATION FACILITY
ELECTRIC POWER LOAD LIST
Information as of Date: |  |  | 2010-03-31
Phase 1 Project Loads
Building | Tag | Description | Voltage | Load |  | Running |  |  | Comments | Supply
Headworks Building - HW |  |  |  | hp | KW | y/n | hp | KW
|  | Screen No. 1 | 480v, 3p | 2 | 1.492 | y | 2 | 1.492
|  | Screen No. 2 | 480v, 3p | 2 | 1.492 |  |  |  | Standby
|  | Washer/Compactor No. 1 | 480v, 3p | 5 | 3.73 | y | 5 | 3.73
|  | Washer/Compactor No. 2 | 480v, 3p | 5 | 3.73 |  |  |  | Standby
|  | Grit Collector No. 1 | 480v, 3p | 1 | 0.746 | y | 1 | 0.746
|  | Grit Collector No. 2 | 480v, 3p | 1 | 0.746 |  |  |  | Standby
|  | Grit Pump No. 1 | 480v, 3p | 7.5 | 5.595 | y | 7.5 | 5.595
|  | Grit Pump No. 2 | 480v, 3p | 7.5 | 5.595 |  |  |  | Standby
|  | Grit Classifier No. 1 | 480v, 3p | 1 | 0.746 | y | 1 | 0.746
|  | Screenings Conveyor No. 1 | 480v, 3p | 3 | 2.238 | y | 3 | 2.238
|  | Interior Lighting | 120v, 1p |  | 4.15 | y |  | 4.15
|  | Exterior Lighting | 277v, 1p |  | 1.058 | y |  | 1.058
|  | HVAC | 480v, 3p | 10 | 7.46 | y | 10 | 7.46
|  | Process instruments, controls, valves | 120v, 1p |  | 1 | y |  | 1
|  | Sampler | 120v, 1p |  | 0.5 | y |  | 0.5
| Subtotals |  | Connected | 45 | hp
|  |  | Connected |  | 40.278 | KW
|  |  | Running |  |  |  | 29.5 | hp
|  |  | Running |  |  |  |  | 28.715 | KW
Building | Tag | Description | Voltage | Load |  | Running |  |  | Comments | Supply
Process Basins |  |  |  | hp | KW | y/n | hp | KW
Aeration Basins - AB
Aeration Basin No.1
Fine Bubble Diffuser System No. 1
|  | Propeller Mixer No. 1 | 480v, 3p | 10 | 7.46 | y | 10 | 7.46
|  | Propeller Mixer No. 2 | 480v, 3p | 10 | 7.46 | y | 10 | 7.46
Aeration Basin No.2
Fine Bubble Diffuser System No. 2
|  | Propeller Mixer No. 2 | 480v, 3p | 10 | 7.46 | y | 10 | 7.46
|  | Propeller Mixer No. 3 | 480v, 3p | 10 | 7.46 | y | 10 | 7.46
Aeration Basin No.3
Fine Bubble Diffuser System No. 3
|  | Propeller Mixer No. 4 | 480v, 3p | 10 | 7.46 | y | 10 | 7.46
|  | Propeller Mixer No. 5 | 480v, 3p | 10 | 7.46 | y | 10 | 7.46
|  | Process instruments, controls, valves | 120v, 1p |  | 5 | y |  | 5
Aerobic Digesters - AD
Aerobic Digester Basin No. 1
|  | Process instruments, controls, valves | 120v, 1p |  | 3 | y |  | 3
Aerobic Digester Basin No. 2
|  | Process instruments, controls, valves | 120v, 1p |  | 3 | y |  | 3
Aerobic Digester Basin No. 3
|  | Process instruments, controls, valves | 120v, 1p |  | 3 | y |  | 3
|  | Interior Lighting | 120v, 1p |  | 27.6667 | y |  | 27.6667
|  | Exterior Lighting | 277v, 1p |  | 2.82 | y |  | 2.82
|  | HVAC | 480v, 3p | 60 | 44.76 | y | 60 | 44.76
|  | Process instruments, controls, valves | 120v, 1p |  | 8.25 | y |  | 8.25
| Subtotals |  | Connected | 120 | hp
|  |  | Connected |  | 142.2567 | KW
|  |  | Running |  |  |  | 120 | hp
|  |  | Running |  |  |  |  | 142.2567 | KW
Building | Tag | Description | Voltage | Load |  | Running |  |  | Comments | Supply
Secondary Clarifier Complex - SC |  |  |  | hp | KW | y/n | hp | KW
Secondary Clarifier No. 1
|  | Clarifier Drive No. 1 | 480v, 3p | 1.5 | 1.119 | y | 1.5 | 1.119
|  | Process instruments, controls, valves | 120v, 1p |  | 0.5 | y |  | 0.5
Secondary Clarifier No. 2
|  | Clarifier Drive No. 2 | 480v, 3p | 1.5 | 1.119 | y | 1.5 | 1.119
|  | Process instruments, controls, valves | 120v, 1p |  | 0.5 | y |  | 0.5
A-Basin Recycle Pumping
|  | Recycle Pump No. 1 | 480v, 3p | 50 | 37.3 | y | 50 | 37.3 | VFD
|  | Recycle Pump No. 2 | 480v, 3p | 50 | 37.3 | y | 50 | 37.3 | VFD
|  | Recycle Pump No. 3 | 480v, 3p | 50 | 37.3 | y | 50 | 37.3 | VFD
|  | Recycle Pump No. 4 (spare) | 480v, 3p | 50 | 37.3 |  |  |  | VFD, standby
|  | Process instruments, controls, valves | 120v, 1p |  | 5 | y |  | 5
Return Activated Sludge (RAS) Pumping
|  | RAS Pump No. 1 | 480v, 3p | 40 | 29.84 | y | 40 | 29.84 | VFD
|  | RAS Pump No. 2 | 480v, 3p | 40 | 29.84 | y | 40 | 29.84 | VFD
|  | RAS Pump No. 3 (spare) | 480v, 3p | 40 | 29.84 |  |  |  | VFD, standby
|  | Process instruments, controls, valves | 120v, 1p |  | 5 | y |  | 5
|  | Scum Pump No. 1 | 480v, 3p | 2 | 1.492 | y | 2 | 1.492
|  | Scum Pump No. 2 | 480v, 3p | 2 | 1.492 | y | 2 | 1.492
|  | Process instruments, controls, valves | 120v, 1p |  | 5 | y |  | 5
Waste Activated Sludge (WAS) Pumping
|  | WAS Pump No. 1 | 480v, 3p | 7.5 | 5.595 | y | 7.5 | 5.595 | VFD
|  | WAS Pump No. 2 | 480v, 3p | 7.5 | 5.595 | y | 7.5 | 5.595 | VFD
|  | WAS Pump No. 3 (spare) | 480v, 3p | 7.5 | 5.595 |  |  |  | VFD, standby
|  | Process instruments, controls, valves | 120v, 1p |  | 5 | y |  | 5
Digested Sludge Pumping
|  | Digested Sludge Pump No. 1 | 480v, 3p | 5 | 3.73 | y | 5 | 3.73 | VFD
|  | Digested Sludge Pump No. 2 | 480v, 3p | 5 | 3.73 | y | 5 | 3.73 | VFD
|  | Digested Sludge Pump No. 3 | 480v, 3p | 5 | 3.73 | y | 5 | 3.73 | VFD
|  | Process instruments, controls, valves | 120v, 1p |  | 5 | y |  | 5
Disinfection System
|  | UV Bank 1A | 480v, 3p |  | 32 | y |  | 32
|  | Process instruments and controls | 120v, 1p |  | 2 | y |  | 2
|  | UV Bank 2A | 480v, 3p |  | 32 |  |  |  | Standby
|  | Process instruments and controls | 120v, 1p |  | 2 |  |  |  | Standby
Plant Water System
|  | Booster Pump No. 1 | 480v, 3p | 5 | 3.73 | y | 5 | 3.73 | Jockey pump
|  | Booster Pump No. 2 | 480v, 3p | 15 | 11.19 | y | 15 | 11.19 | Duty/service pump
|  | Booster Pump No. 3 | 480v, 3p | 15 | 11.19 | y | 15 | 11.19 | Duty/service pump
|  | Booster Pump No. 4 | 480v, 3p | 25 | 18.65 | y | 25 | 18.65 | Duty/service pump
|  | Process instruments and controls | 120v, 1p |  | 5 | y |  | 5
A-Basin/Plant Drain Pump Station
|  | Pump No. 1 | 480v, 3p | 7.5 | 5.595 | y | 7.5 | 5.595
|  | Pump No. 2 | 480v, 3p | 7.5 | 5.595 | y | 7.5 | 5.595
|  | Process instruments and controls | 120v, 1p |  | 0.5 | y |  | 0.5
On-Site Domestic WW Pump Station
|  | Pump No. 1 | 480v, 3p | 1 | 0.746 | y | 1 | 0.746
|  | Pump No. 2 | 480v, 3p | 1 | 0.746 | y | 1 | 0.746
|  | Process instruments and controls | 120v, 1p |  | 0.5 | y |  | 0.5
|  | Interior Lighting | 120v, 1p |  | 26.975 | y |  | 26.975
|  | Exterior Lighting | 277v, 1p |  | 1.466 | y |  | 1.466
|  | HVAC | 480v, 3p | 40 | 29.84 | y | 40 | 29.84
|  | Process instruments, controls, valves | 120v, 1p |  | 5 | y |  | 5
| Subtotals |  | Connected | 481.5 | hp
|  |  | Connected |  | 492.64 | KW
|  |  | Running |  |  |  | 384 | hp
|  |  | Running |  |  |  |  | 385.905 | KW
Building | Tag | Description | Voltage | Load |  | Running |  |  | Comments | Supply
Biosolids Thickening and Dewatering - BH |  |  |  | hp | KW | y/n | hp | KW
Sludge Thickening
|  | Rotary Drum Thickener No. 1 | 480v, 3p | 2.5 | 1.865 | y | 2.5 | 1.865
|  | Washwater Booster Pump No. 1 | 480v, 3p | 5 | 3.73 | y | 5 | 3.73
|  | Rotary Drum Thickener No. 2 | 480v, 3p | 2.5 | 1.865 |  |  |  | Standby
|  | Washwater Booster Pump No. 2 | 480v, 3p | 5 | 3.73 |  |  |  | Standby
|  | Thickened Sludge Pump No. 1 | 480v, 3p | 5 | 3.73 | y | 5 | 3.73 | VFD
|  | Thickened Sludge Pump No. 2 | 480v, 3p | 5 | 3.73 |  |  |  | VFD, standby
|  | Process instruments, controls, valves | 120v, 1p |  | 0.5 | y |  | 0.5
Sludge Dewatering
|  | Belt Press Feed Pump No. 1 | 480v, 3p | 7.5 | 5.595 | y | 7.5 | 5.595 | VFD
|  | Belt Press Feed Pump No. 2 (spare) | 480v, 3p | 7.5 | 5.595 |  |  |  | VFD, standby
|  | Belt Filter Press No. 1 | 480v, 3p | 3 | 2.238 | y | 3 | 2.238
|  | Washwater Booster Pump No. 1 | 480v, 3p | 5 | 3.73 | y | 5 | 3.73
|  | Belt Filter Press No. 2 (spare) | 480v, 3p | 3 | 2.238 | y | 3 | 2.238 | Standby
|  | Washwater Booster Pump No. 2 | 480v, 3p | 5 | 3.73 |  |  |  | Standby
Conveyors
|  | Dewatered Cake Conveyor No. 1 | 480v, 3p | 3 | 2.238 | y | 3 | 2.238
|  | Cross conveyor No. 1 | 480v, 3p | 7.5 | 5.595 | y | 7.5 | 5.595
|  | Distribution Conveyor No. 1 | 480v, 3p | 7.5 | 5.595 | y | 7.5 | 5.595
|  | Distribution Conveyor No. 2 | 480v, 3p | 7.5 | 5.595 | y | 7.5 | 5.595
|  | Process instruments, controls, valves | 120v, 1p |  | 2 | y |  | 2
|  | Polymer Feed System No. 1 | 120v, 1p |  | 2 | y |  | 2
|  | Polymer Feed System No. 2 | 120v, 1p |  | 2 | y |  | 2
|  | Interior Lighting | 120v, 1p |  | 16.6 | y |  | 16.6
|  | Exterior Lighting | 277v, 1p |  | 1.09 | y |  | 1.09
|  | HVAC | 480v, 3p | 40 | 29.84 | y | 40 | 29.84
|  | Process instruments, controls, valves | 120v, 1p |  | 5 | y |  | 5
| Subtotals |  | Connected | 121.5 | hp
|  |  | Connected |  | 119.829 | KW
|  |  | Running |  |  |  | 96.5 | hp
|  |  | Running |  |  |  |  | 101.179 | KW
Building | Tag | Description | Voltage | Load |  | Running |  |  | Comments | Supply
Blower Building - BB |  |  |  | hp | KW | y/n | hp | KW
|  | Aeration Blower No. 1 | 480v, 3p | 150 | 111.9 | y | 150 | 111.9
|  | Aeration Blower No. 2 | 480v, 3p | 150 | 111.9 | y | 150 | 111.9
|  | Aeration Blower No. 3 | 480v, 3p | 150 | 111.9 | y | 150 | 111.9
|  | Aeration Blower No. 4 (spare) | 480v, 3p | 150 | 111.9 |  |  |  | Standby
|  | Digester Blower No. 1 | 480v, 3p | 100 | 74.6 | y | 100 | 74.6
|  | Digester Blower No. 2 | 480v, 3p | 100 | 74.6 | y | 100 | 74.6
|  | Digester Blower No. 3 | 480v, 3p | 100 | 74.6 | y | 100 | 74.6
|  | Digester Blower No. 4 (spare) | 480v, 3p | 100 | 74.6 |  |  |  | Standby
|  | Interior Lighting | 120v, 1p |  | 4.15 | y |  | 4.15
|  | Exterior Lighting | 277v, 1p |  | 0.526 | y |  | 0.526
|  | HVAC | 480v, 3p | 30 | 27.38 | y | 30 | 27.38
|  | Process instruments, controls, valves | 120v, 1p |  | 4 | y |  | 4
| Subtotals |  | Connected | 1030 | hp
|  |  | Connected |  | 782.056 | KW
|  |  | Running |  |  |  | 780 | hp
|  |  | Running |  |  |  |  | 595.556 | KW
Building | Tag | Description | Voltage | Load |  | Running |  |  | Comments | Supply
Operations Building - OP |  |  |  | hp | KW | y/n | hp | KW
Potable water system
|  | Well Pump No.1 | 240v, 1p | 0.5 | 0.373 | y | 0.5 | 0.373
|  | Softener Feed Pump No. 1 | 120v, 1p | 0.5 | 0.373 | y | 0.5 | 0.373
|  | RO Feed Pump No.1 | 480v, 3p | 1 | 0.746 | y | 1 | 0.746
|  | RO Permeate Pump No. 1 | 120v, 1p | 0.5 | 0.373 | y | 0.5 | 0.373
|  | Finish Water Pump No. 1 | 480v, 3p | 5 | 3.73 | y | 5 | 3.73
|  | Process instruments and controls | 120v, 1p |  | 1.5 | y |  | 1.5
|  | Lab equipment | 120v, 1p |  | 5 | y |  | 5
|  | Lab appliances | 240v, 1p |  | 5 | y |  | 5
|  | Receptacles | 120v, 1p |  | 10 | y |  | 10
|  | Water heater | 240v, 1p |  | 5 | y |  | 5
|  | Misc computers, appliances, etc. | 120v, 1p |  | 25 | y |  | 25
|  | Interior Lighting | 120v, 1p |  | 5 | y |  | 5
|  | Exterior Lighting | 277v, 1p |  | 1.278 | y |  | 1.278
|  | HVAC | 480v, 3p | 30 | 27.38 | y | 30 | 27.38
| Subtotals |  | Connected | 37.5 | hp
|  |  | Connected |  | 90.753 | KW
|  |  | Running |  |  |  | 37.5 | hp
|  |  | Running |  |  |  |  | 90.753 | KW
Building | Tag | Description | Voltage | Load |  | Running |  |  | Comments | Supply
Equipment and Maintenance Building - EM |  |  |  | hp | KW | y/n | hp | KW
|  | Tools, equipment, etc. | 120v, 1p |  | 5 | y |  | 5
|  | Receptacles | 120v, 1p |  | 10 | y |  | 10
|  | Water heater |  |  |  | y
|  | Interior Lighting | 120v, 1p |  | 7.5 | y |  | 7.5
|  | Exterior Lighting | 277v, 1p |  | 0.696 | y |  | 0.696
|  | HVAC | 480v, 3p | 30 | 27.38 | y | 30 | 27.38
| Subtotals |  | Connected | 30 | hp
|  |  | Connected |  | 50.576 | KW
|  |  | Running |  |  |  | 30 | hp
|  |  | Running |  |  |  |  | 50.576 | KW
Phase 1 Project Totals
|  |  | Connected | 1865.5 | hp
|  |  | Connected |  | 1718.3887 | KW
|  |  | Powered |  |  |  | 1477.5 | hp
|  |  | Powered |  |  |  |  | 1394.9407 | KW
Future Build-out Loads
Building | Tag | Description | Voltage | Load |  | Running |  |  | Comments | Supply
Future Primary Clarifier Complex No. 1 |  |  |  | hp | KW | y/n | hp | KW
Primary Clarifier No. 1
|  | Clarifier Drive No. 1 | 480v, 3p | 1.5 | 1.119 | y | 1.5 | 1.119
|  | Process instruments, controls, valves | 120v, 1p |  | 0.5 | y |  | 0.5
Primary Clarifier No. 2
|  | Clarifier Drive No. 2 | 480v, 3p | 1.5 | 1.119 | y | 1.5 | 1.119
|  | Process instruments, controls, valves | 120v, 1p |  | 0.5 | y |  | 0.5
|  | Scum Pump No. 1 | 480v, 3p | 2 | 1.492 | y | 2 | 1.492
|  | Scum Pump No. 2 | 480v, 3p | 2 | 1.492 | y | 2 | 1.492
|  | Process instruments, controls, valves | 120v, 1p |  | 0.5 | y |  | 0.5
|  | Primary Sludge Pump No. 1 | 480v, 3p | 30 | 22.38 | y | 30 | 22.38
|  | Primary Sludge Pump No. 2 | 480v, 3p | 30 | 22.38 | y | 30 | 22.38
|  | Process instruments, controls, valves | 120v, 1p |  | 0.5 | y |  | 0.5
|  | Interior Lighting | 120v, 1p |  | 12.45 | y |  | 12.45
|  | Exterior Lighting | 277v, 1p |  | 1.316 | y |  | 1.316
|  | HVAC | 480v, 3p | 40 | 29.84 | y | 40 | 29.84
| Subtotals |  | Connected | 107 | hp
|  |  | Connected |  | 95.588 | KW
|  |  | Running |  |  |  | 107 | hp
|  |  | Running |  |  |  |  | 95.588 | KW
Future Primary Clarifier Complex No. 2
Assume same as Future Primary Clarifier Complex No. 1
| Subtotals |  | Connected | 107 | hp
|  |  | Connected |  | 95.588 | KW
|  |  | Running |  |  |  | 107 | hp
|  |  | Running |  |  |  |  | 95.588 | KW
Future Process Basins
Assume same as Phase 1 A-Basins and Digester Basins
| Subtotals |  | Connected | 120 | hp
|  |  | Connected |  | 142.2567 | KW
|  |  | Running |  |  |  | 120 | hp
|  |  | Running |  |  |  |  | 142.2567 | KW
Future Secondary Clarifier Complex
Assume same as Phase 1 Secondary Clarifier Complex
| Subtotals |  | Connected | 481.5 | hp
|  |  | Connected |  | 492.64 | KW
|  |  | Running |  |  |  | 384 | hp
|  |  | Running |  |  |  |  | 385.905 | KW
Building | Tag | Description | Voltage | Load |  | Running |  |  | Comments | Supply
Future Biosolids Thickening and Dewatering |  |  |  | hp | KW | y/n | hp | KW
Sludge Thickening
|  | Rotary Drum Thickener No. 3 | 480v, 3p | 2.5 | 1.865 | y | 2.5 | 1.865
|  | Washwater Booster Pump No. 5 | 480v, 3p | 5 | 3.73 | y | 5 | 3.73
|  | Thickened Sludge Pump No. 3 | 480v, 3p | 5 | 3.73 | y | 5 | 3.73 | VFD
|  | Process instruments, controls, valves | 120v, 1p |  | 0.5 | y |  | 0.5
Sludge Dewatering
|  | Belt Press Feed Pump No. 3 | 480v, 3p | 7.5 | 5.595 | y | 7.5 | 5.595 | VFD
|  | Belt Filter Press No. 3 | 480v, 3p | 3 | 2.238 | y | 3 | 2.238
|  | Washwater Booster Pump No. 6 | 480v, 3p | 5 | 3.73 | y | 5 | 3.73
Conveyors
|  | Dewatered Cake Conveyor No. 2 | 480v, 3p | 3 | 2.238 | y | 3 | 2.238
|  | Process instruments, controls, valves | 120v, 1p |  | 2 | y |  | 2
|  | Polymer Feed System No. 3 | 120v, 1p |  | 2 | y |  | 2
|  | Polymer Feed System No. 4 | 120v, 1p |  | 2 | y |  | 2
|  | Interior Lighting | 120v, 1p |  | 8.3 | y |  | 8.3
|  | Exterior Lighting | 277v, 1p |  | 0.545 | y |  | 0.545
|  | HVAC | 480v, 3p | 20 | 14.92 | y | 20 | 14.92
|  | Process instruments, controls, valves | 120v, 1p |  | 5 | y |  | 5
| Subtotals |  | Connected | 51 | hp
|  |  | Connected |  | 58.391 | KW
|  |  | Running |  |  |  | 51 | hp
|  |  | Running |  |  |  |  | 58.391 | KW
Future Blower Building
Assume same as Phase 1 Blower Building
| Subtotals |  | Connected | 1030 | hp
|  |  | Connected |  | 782.056 | KW
|  |  | Running |  |  |  | 780 | hp
|  |  | Running |  |  |  |  | 595.556 | KW
Building | Tag | Description | Voltage | Load |  | Running |  |  | Comments | Supply
Future Headworks Building |  |  |  | hp | KW | y/n | hp | KW
Change out screens and compactors for larger units - loads below are in addition to Phase 1 loads
|  | Screen No. 1 | 480v, 3p | 1 | 0.746 | y | 1 | 0.746
|  | Screen No. 2 | 480v, 3p | 1 | 0.746 |  |  |  | Standby
|  | Washer/Compactor No. 1 | 480v, 3p | 2.5 | 1.865 | y | 2.5 | 1.865
|  | Washer/Compactor No. 2 | 480v, 3p | 2.5 | 1.865 |  |  |  | Standby
| Subtotals |  | Connected | 7 | hp
|  |  | Connected |  | 5.222 | KW
|  |  | Running |  |  |  | 3.5 | hp
|  |  | Running |  |  |  |  | 2.611 | KW
Future Build-Out Totals
(Phase 1 + Future Expansions)
|  |  | Connected | 3769 | hp
|  |  | Connected |  | 3390.1303 | KW
|  |  | Powered |  |  |  | 3030 | hp
|  |  | Powered |  |  |  |  | 2770.8363 | KW